## Data
Spread Sheet to Calculate Water Tank Storage Temperature over one day
Assumes that the tank is fully mixed.
Initialization Data | [10 empty] | Solar Collector Data
Initial Temperature in Water Tank |  |  |  | 52 | C | [5 empty] | SRCC # | 2010115A
Volume of Storage Tank |  |  |  | 80 | gallons | 0.30283 | m^3 |  |  |  | Heliodyne Gobi
Density of Water |  |  |  | 990 | kg/m^3 | [5 empty] | Gross Area |  |  | 3.732 | m^2 | 40.17 | ft^2
Specific Heat of Water |  |  |  | 4180 | J/kg-k | [5 empty] | Tested Volume Flow |  |  | 22.2 | ml/s-m^2
Temperature of City Water |  |  |  | 15 | C | [5 empty] | Volume Flow per collector |  |  | 82.8504 | m^3/s
Number of Solar Panels |  |  |  | 1 | [6 empty] | efficiency Y-intercept |  |  | 0.752
Flow rate of water through all panels |  |  |  | 82.8504 | m^3/s | [5 empty] | efficiency slope |  |  | -4.023 | W/m^2-C
Temperature of Air Around Tank |  |  |  | 19 | C | [5 empty] | Incident Angle Modifier slope |  |  | -0.17
Tank Loss Coefficient |  |  |  | 3 | W/C
Mass of Water in Tank |  |  |  | 299.8046 | kg
Site Data
Collector Tilt (beta) |  |  | 15 | degrees | 0.2618 | radians
Surface Azimuth |  |  | 0 | degrees | 0 | radians
Latitude |  |  | 32 | degrees | 0.55851 | radians
Day of year | May 1st |  | 121
declination (delta) |  |  | 14.9009 | degrees | 0.26007 | radians
Direct Beam Flux |  |  | 750 | W/m^2
term1 of cos(theta) |  |  | 0.13162
term2 of cos(theta) |  |  | 0.056442
Solar Time | Hour Angle (degrees) | Hour Angle (radians) | term 3 of cos(theta) | term 4 of cos(theta) | term 5 of cos(theta) | cos(theta) | theta (radians) | theta (degrees) | 1/cos(theta) - 1 | Incident Angle Modifier | Ambient Temperature (C ) | G sub T (W/m^2) | Water Draw (gpm) | Water Draw (m^3/s) | Tank Temperature at start of 5 minute period (C ) | Useful Gain (J) | Load (J) | Losses to Ambient (J) | Tank Temperatuer at end of 5 minute period | Energy striking collector | panel efficiency | Tank Temp (F)
6:00 | -90 | -1.5708 | 4.8472e-17 | 8.1158e-18 | 0 | 0.075183 | 1.4955 | 85.6883 | 12.3009 | -1.0912 | 13.5224 | 56.387 | 0 | 0 | 52 | 0 | 0 | 29700 | 51.9763 | 63130.9378 | 0 | 125.6
6:05 | -88.75 | -1.549 | 0.017269 | 0.0028914 | 0 | 0.095343 | 1.4753 | 84.5289 | 9.4885 | -0.61304 | 13.627 | 71.5072 | 0 | 0 | 51.9763 | 0 | 0 | 29678.6703 | 51.9526 | 80059.4106 | 0 | 125.5573
6:10 | -87.5 | -1.5272 | 0.034529 | 0.0057814 | 0 | 0.11549 | 1.455 | 83.3679 | 7.6585 | -0.30195 | 13.7322 | 86.6201 | 0 | 0 | 51.9526 | 0 | 0 | 29657.356 | 51.929 | 96979.8263 | 0 | 125.5147
6:15 | -86.25 | -1.5053 | 0.051773 | 0.0086686 | 0 | 0.13562 | 1.4348 | 82.2053 | 6.3733 | -0.083458 | 13.838 | 101.7186 | 0 | 0 | 51.929 | 0 | 0 | 29636.0569 | 51.9053 | 113884.1318 | 0 | 125.4721
6:20 | -85 | -1.4835 | 0.068993 | 0.011552 | 0 | 0.15573 | 1.4144 | 81.041 | 5.4215 | 0.078349 | 13.9443 | 116.7955 | 0 | 0 | 51.9053 | 0 | 0 | 29614.7731 | 51.8817 | 130764.2815 | 0 | 125.4295
6:25 | -83.75 | -1.4617 | 0.08618 | 0.014429 | 0 | 0.17579 | 1.3941 | 79.8753 | 4.6886 | 0.20295 | 14.0512 | 131.8437 | 0.5 | 3.1545e-05 | 51.8817 | 0 | 1444359.2058 | 29593.5047 | 50.7055 | 147612.2414 | 0 | 125.387
6:30 | -82.5 | -1.4399 | 0.10333 | 0.0173 | 0 | 0.19581 | 1.3737 | 78.7081 | 4.107 | 0.3018 | 14.1585 | 146.856 | 0.5 | 3.1545e-05 | 50.7055 | 0 | 1398298.1836 | 28534.9544 | 49.5669 | 164419.9928 | 0 | 123.2699
6:35 | -81.25 | -1.4181 | 0.12042 | 0.020163 | 0 | 0.21577 | 1.3533 | 77.5395 | 3.6346 | 0.38211 | 14.2662 | 161.8252 | 0.5 | 3.1545e-05 | 49.5669 | 0 | 1353709.6481 | 27510.2441 | 48.4648 | 181179.536 | 0 | 121.2205
6:40 | -80 | -1.3963 | 0.13746 | 0.023016 | 0 | 0.23566 | 1.3329 | 76.3695 | 3.2434 | 0.44862 | 14.3743 | 176.7443 | 0 | 0 | 48.4648 | 0 | 0 | 26518.2919 | 48.4436 | 197882.8946 | 0 | 119.2366
6:45 | -78.75 | -1.3744 | 0.15443 | 0.025857 | 0 | 0.25547 | 1.3125 | 75.1983 | 2.9143 | 0.50457 | 14.4827 | 191.606 | 0 | 0 | 48.4436 | 0 | 0 | 26499.2473 | 48.4225 | 214522.1185 | 0 | 119.1985
6:50 | -77.5 | -1.3526 | 0.17133 | 0.028687 | 0 | 0.2752 | 1.292 | 74.0258 | 2.6337 | 0.55228 | 14.5913 | 206.4034 | 0.3 | 1.8927e-05 | 48.4225 | 0 | 785333.837 | 26480.2163 | 47.7747 | 231089.2883 | 0 | 119.1604
6:55 | -76.25 | -1.3308 | 0.18815 | 0.031503 | 0 | 0.29484 | 1.2715 | 72.8521 | 2.3917 | 0.59341 | 14.7001 | 221.1294 | 0.2 | 1.2618e-05 | 47.7747 | 0 | 513408.2157 | 25897.1949 | 47.3443 | 247576.5192 | 0 | 117.9944
7:00 | -75 | -1.309 | 0.20488 | 0.034304 | 0 | 0.31437 | 1.251 | 71.6773 | 2.181 | 0.62923 | 14.809 | 235.777 | 0.2 | 1.2618e-05 | 47.3443 | 0 | 506666.898 | 25509.8814 | 46.9197 | 263975.9639 | 0 | 117.2198
7:05 | -73.75 | -1.2872 | 0.22151 | 0.037089 | 0 | 0.33379 | 1.2305 | 70.5013 | 1.9959 | 0.66069 | 14.9181 | 250.3392 | 0 | 0 | 46.9197 | 0 | 0 | 25127.6874 | 46.8996 | 280279.8172 | 0 | 116.4554
7:10 | -72.5 | -1.2654 | 0.23804 | 0.039856 | 0 | 0.35308 | 1.2099 | 69.3243 | 1.8322 | 0.68852 | 15.0272 | 264.8091 | 0 | 0 | 46.8996 | 0 | 0 | 25109.6414 | 46.8796 | 296480.3195 | 0 | 116.4193
7:15 | -71.25 | -1.2435 | 0.25445 | 0.042604 | 0 | 0.37224 | 1.1894 | 68.1462 | 1.6864 | 0.71331 | 15.1362 | 279.1798 | 0 | 0 | 46.8796 | 0 | 0 | 25091.6084 | 46.8595 | 312569.7601 | 0 | 116.3832
7:20 | -70 | -1.2217 | 0.27074 | 0.045332 | 0 | 0.39126 | 1.1688 | 66.9671 | 1.5558 | 0.73551 | 15.2452 | 293.4445 | 0 | 0 | 46.8595 | 0 | 0 | 25073.5883 | 46.8395 | 328540.4813 | 0 | 116.3472
7:25 | -68.75 | -1.1999 | 0.28691 | 0.048038 | 0 | 0.41013 | 1.1482 | 65.7871 | 1.4383 | 0.7555 | 15.3541 | 307.5964 | 0 | 0 | 46.8395 | 0 | 0 | 25055.5812 | 46.8195 | 344384.8819 | 0 | 116.3112
7:30 | -67.5 | -1.1781 | 0.30293 | 0.050721 | 0 | 0.42884 | 1.1276 | 64.6061 | 1.3319 | 0.77358 | 15.4628 | 321.6286 | 0.6 | 3.7854e-05 | 46.8195 | 0 | 1495339.3859 | 25037.587 | 45.6063 | 360095.4209 | 0 | 116.2752
7:35 | -66.25 | -1.1563 | 0.31882 | 0.05338 | 0 | 0.44738 | 1.107 | 63.4243 | 1.2352 | 0.79001 | 15.5713 | 335.5347 | 0.6 | 3.7854e-05 | 45.6063 | 0 | 1438325.2494 | 23945.6962 | 44.4395 | 375664.6209 | 0 | 114.0914
7:40 | -65 | -1.1345 | 0.33455 | 0.056014 | 0 | 0.46574 | 1.0863 | 62.2416 | 1.1471 | 0.80499 | 15.6796 | 349.3079 | 0.6 | 3.7854e-05 | 44.4395 | 0 | 1383490.0889 | 22895.5355 | 43.3172 | 391085.0718 | 0 | 111.9911
7:45 | -63.75 | -1.1126 | 0.35012 | 0.058621 | 0 | 0.48392 | 1.0657 | 61.0581 | 1.0664 | 0.8187 | 15.7875 | 362.9416 | 0 | 0 | 43.3172 | 0 | 0 | 21885.51 | 43.2998 | 406349.4342 | 0 | 109.971
7:50 | -62.5 | -1.0908 | 0.36552 | 0.061201 | 0 | 0.50191 | 1.045 | 59.8738 | 0.99241 | 0.83129 | 15.895 | 376.4295 | 0 | 0 | 43.2998 | 232779.306 | 0 | 21869.7925 | 43.4681 | 421450.4433 | 0.55233 | 109.9396
7:55 | -61.25 | -1.069 | 0.38075 | 0.063751 | 0 | 0.51969 | 1.0243 | 58.6888 | 0.92424 | 0.84288 | 16.0021 | 389.765 | 0 | 0 | 43.4681 | 245847.2107 | 0 | 22021.2616 | 43.6467 | 436380.9117 | 0.56338 | 110.2425
8:00 | -60 | -1.0472 | 0.3958 | 0.066271 | 0 | 0.53726 | 1.0036 | 57.503 | 0.86131 | 0.85358 | 16.1087 | 402.9419 | 0 | 0 | 43.6467 | 258746.7412 | 0 | 22182.0069 | 43.8354 | 451133.7333 | 0.57355 | 110.564
8:05 | -58.75 | -1.0254 | 0.41066 | 0.068759 | 0 | 0.55461 | 0.98291 | 56.3165 | 0.80308 | 0.86348 | 16.2148 | 415.9538 | 0 | 0 | 43.8354 | 271471.8213 | 0 | 22351.9009 | 44.0342 | 465701.8866 | 0.58293 | 110.9038
8:10 | -57.5 | -1.0036 | 0.42533 | 0.071214 | 0 | 0.57173 | 0.96219 | 55.1293 | 0.74909 | 0.87265 | 16.3203 | 428.7946 | 0 | 0 | 44.0342 | 284016.4582 | 0 | 22530.8116 | 44.2429 | 480078.4379 | 0.5916 | 111.2616
8:15 | -56.25 | -0.98175 | 0.43979 | 0.073636 | 0 | 0.58861 | 0.94146 | 53.9415 | 0.69892 | 0.88118 | 16.4252 | 441.4582 | 0 | 0 | 44.2429 | 296374.7446 | 0 | 22718.603 | 44.4613 | 494256.5448 | 0.59964 | 111.6372
8:20 | -55 | -0.95993 | 0.45405 | 0.076022 | 0 | 0.60525 | 0.92071 | 52.7531 | 0.65221 | 0.88912 | 16.5294 | 453.9384 | 0 | 0 | 44.4613 | 308540.8619 | 0 | 22915.1349 | 44.6892 | 508229.4593 | 0.60709 | 112.0303
8:25 | -53.75 | -0.93811 | 0.46808 | 0.078373 | 0 | 0.62164 | 0.89996 | 51.5641 | 0.60865 | 0.89653 | 16.6329 | 466.2295 | 0 | 0 | 44.6892 | 320509.0827 | 0 | 23120.2631 | 44.9265 | 521990.5309 | 0.61401 | 112.4405
8:30 | -52.5 | -0.9163 | 0.4819 | 0.080686 | 0 | 0.63777 | 0.8792 | 50.3745 | 0.56797 | 0.90345 | 16.7356 | 478.3255 | 0 | 0 | 44.9265 | 332273.774 | 0 | 23333.8391 | 45.173 | 535533.2103 | 0.62045 | 112.8677
8:35 | -51.25 | -0.89448 | 0.49548 | 0.082961 | 0 | 0.65363 | 0.85843 | 49.1843 | 0.52992 | 0.90991 | 16.8375 | 490.2207 | 0 | 0 | 45.173 | 343829.3992 | 0 | 23555.7109 | 45.4286 | 548851.0517 | 0.62645 | 113.3114
8:40 | -50 | -0.87266 | 0.50883 | 0.085196 | 0 | 0.66921 | 0.83765 | 47.9937 | 0.49429 | 0.91597 | 16.9385 | 501.9094 | 0 | 0 | 45.4286 | 355170.5213 | 0 | 23785.7222 | 45.693 | 561937.7167 | 0.63205 | 113.7714
8:45 | -48.75 | -0.85085 | 0.52194 | 0.08739 | 0 | 0.68451 | 0.81686 | 46.8025 | 0.46089 | 0.92165 | 17.0386 | 513.386 | 0 | 0 | 45.693 | 366291.8053 | 0 | 24023.7131 | 45.9661 | 574786.9767 | 0.63727 | 114.2474
8:50 | -47.5 | -0.82903 | 0.5348 | 0.089543 | 0 | 0.69953 | 0.79606 | 45.6109 | 0.42954 | 0.92698 | 17.1377 | 524.6452 | 0 | 0 | 45.9661 | 377188.0207 | 0 | 24269.5202 | 46.2478 | 587392.7161 | 0.64214 | 114.739
8:55 | -46.25 | -0.80721 | 0.54741 | 0.091654 | 0 | 0.71424 | 0.77526 | 44.4189 | 0.40009 | 0.93199 | 17.2358 | 535.6814 | 0 | 0 | 46.2478 | 387854.044 | 0 | 24522.9761 | 46.5377 | 599748.9353 | 0.64669 | 115.246
9:00 | -45 | -0.7854 | 0.55975 | 0.093721 | 0 | 0.72865 | 0.75444 | 43.2264 | 0.3724 | 0.93669 | 17.3328 | 546.4896 | 0 | 0 | 46.5377 | 398284.8612 | 0 | 24783.9099 | 46.8357 | 611849.7534 | 0.65095 | 115.7678
9:05 | -43.75 | -0.76358 | 0.57183 | 0.095743 | 0 | 0.74275 | 0.73362 | 42.0336 | 0.34634 | 0.94112 | 17.4287 | 557.0645 | 0 | 0 | 46.8357 | 408475.57 | 0 | 25052.1475 | 47.1417 | 623689.4111 | 0.65493 | 116.3043
9:10 | -42.5 | -0.74176 | 0.58363 | 0.097719 | 0 | 0.75653 | 0.7128 | 40.8403 | 0.32182 | 0.94529 | 17.5235 | 567.4011 | 0 | 0 | 47.1417 | 418421.3826 | 0 | 25327.5111 | 47.4554 | 635262.2733 | 0.65866 | 116.855
9:15 | -41.25 | -0.71995 | 0.59516 | 0.09965 | 0 | 0.76999 | 0.69197 | 39.6468 | 0.29871 | 0.94922 | 17.617 | 577.4945 | 0 | 0 | 47.4554 | 428117.6274 | 0 | 25609.8198 | 47.7765 | 646562.8319 | 0.66214 | 117.4196
9:20 | -40 | -0.69813 | 0.6064 | 0.10153 | 0 | 0.78312 | 0.67113 | 38.4529 | 0.27694 | 0.95292 | 17.7094 | 587.3399 | 0 | 0 | 47.7765 | 437559.7514 | 0 | 25898.8892 | 48.105 | 657585.7086 | 0.6654 | 117.9978
9:25 | -38.75 | -0.67632 | 0.61736 | 0.10337 | 0 | 0.79591 | 0.65029 | 37.2587 | 0.25642 | 0.95641 | 17.8004 | 596.9325 | 0 | 0 | 48.105 | 446743.3227 | 0 | 26194.5322 | 48.4406 | 668325.657 | 0.66845 | 118.5891
9:30 | -37.5 | -0.6545 | 0.62802 | 0.10515 | 0 | 0.80836 | 0.62944 | 36.0643 | 0.23708 | 0.9597 | 17.8901 | 606.2679 | 0 | 0 | 48.4406 | 455664.0321 | 0 | 26496.5582 | 48.7831 | 678777.5655 | 0.6713 | 119.1931
9:35 | -36.25 | -0.63268 | 0.63839 | 0.10689 | 0 | 0.82046 | 0.60859 | 34.8696 | 0.21884 | 0.9628 | 17.9784 | 615.3416 | 0 | 0 | 48.7831 | 464317.6958 | 0 | 26804.7738 | 49.1322 | 688936.4595 | 0.67396 | 119.8095
9:40 | -35 | -0.61087 | 0.64845 | 0.10857 | 0 | 0.8322 | 0.58773 | 33.6747 | 0.20164 | 0.96572 | 18.0653 | 624.1493 | 0.1 | 6.309e-06 | 49.1322 | 472700.2565 | 267336.9159 | 27118.983 | 49.2744 | 698797.504 | 0.67645 | 120.438
9:45 | -33.75 | -0.58905 | 0.6582 | 0.1102 | 0 | 0.84358 | 0.56688 | 32.4796 | 0.18542 | 0.96848 | 18.1508 | 632.6867 | 0.2 | 1.2618e-05 | 49.2744 | 481046.6263 | 536901.8862 | 27246.9929 | 49.2081 | 708356.0057 | 0.6791 | 120.694
9:50 | -32.5 | -0.56723 | 0.66763 | 0.11178 | 0 | 0.8546 | 0.54602 | 31.2845 | 0.17014 | 0.97108 | 18.2347 | 640.9498 | 0.3 | 1.8927e-05 | 49.2081 | 489354.6135 | 803794.6621 | 27187.3113 | 48.9355 | 717607.4151 | 0.68193 | 120.5746
9:55 | -31.25 | -0.54542 | 0.67675 | 0.11331 | 0 | 0.86525 | 0.52515 | 30.0892 | 0.15574 | 0.97352 | 18.3171 | 648.9347 | 0.2 | 1.2618e-05 | 48.9355 | 497617.7786 | 531592.7661 | 26941.9644 | 48.8869 | 726547.3292 | 0.68491 | 120.0839
10:00 | -30 | -0.5236 | 0.68555 | 0.11478 | 0 | 0.87552 | 0.50429 | 28.8938 | 0.14218 | 0.97583 | 18.3979 | 656.6376 | 0.3 | 1.8927e-05 | 48.8869 | 505350.5783 | 796246.9563 | 26898.2156 | 48.6333 | 735171.493 | 0.68739 | 119.9964
10:05 | -28.75 | -0.50178 | 0.69402 | 0.1162 | 0 | 0.88541 | 0.48343 | 27.6984 | 0.12942 | 0.978 | 18.4771 | 664.0548 | 0.1 | 6.309e-06 | 48.6333 | 513029.6419 | 263429.4359 | 26669.9847 | 48.8112 | 743475.802 | 0.69004 | 119.54
10:10 | -27.5 | -0.47997 | 0.70216 | 0.11757 | 0 | 0.89491 | 0.46257 | 26.5031 | 0.11743 | 0.98004 | 18.5547 | 671.1828 | 0.3 | 1.8927e-05 | 48.8112 | 519938.8679 | 794468.2493 | 26830.0867 | 48.5707 | 751456.3036 | 0.69191 | 119.8602
10:15 | -26.25 | -0.45815 | 0.70997 | 0.11887 | 0 | 0.90402 | 0.4417 | 25.3078 | 0.10616 | 0.98195 | 18.6306 | 678.0182 | 0 | 0 | 48.5707 | 527026.3621 | 0 | 26613.6591 | 48.97 | 759109.1996 | 0.69427 | 119.4273
10:20 | -25 | -0.43633 | 0.71744 | 0.12012 | 0 | 0.91274 | 0.42085 | 24.1127 | 0.095598 | 0.98375 | 18.7047 | 684.5577 | 0 | 0 | 48.97 | 533104.1694 | 0 | 26973.041 | 49.3739 | 766430.8477 | 0.69557 | 120.1461
10:25 | -23.75 | -0.41452 | 0.72457 | 0.12132 | 0 | 0.92106 | 0.39999 | 22.9178 | 0.0857 | 0.98543 | 18.7771 | 690.7983 | 0 | 0 | 49.3739 | 538880.3826 | 0 | 27336.5297 | 49.7821 | 773417.7631 | 0.69675 | 120.8731
10:30 | -22.5 | -0.3927 | 0.73135 | 0.12245 | 0 | 0.92898 | 0.37914 | 21.7232 | 0.076447 | 0.987 | 18.8476 | 696.7369 | 0 | 0 | 49.7821 | 544352.3103 | 0 | 27703.9058 | 50.1944 | 780066.6204 | 0.69783 | 121.6078
10:35 | -21.25 | -0.37088 | 0.73778 | 0.12353 | 0 | 0.93649 | 0.3583 | 20.5291 | 0.067812 | 0.98847 | 18.9164 | 702.3707 | 0 | 0 | 50.1944 | 549517.406 | 0 | 28074.9477 | 50.6105 | 786374.2552 | 0.6988 | 122.3499
10:40 | -20 | -0.34907 | 0.74387 | 0.12455 | 0 | 0.9436 | 0.33747 | 19.3355 | 0.059775 | 0.98984 | 18.9832 | 707.6971 | 0 | 0 | 50.6105 | 554373.2692 | 0 | 28449.4326 | 51.0302 | 792337.6653 | 0.69967 | 123.0989
10:45 | -18.75 | -0.32725 | 0.74959 | 0.12551 | 0 | 0.95028 | 0.31665 | 18.1426 | 0.052316 | 0.99111 | 19.0482 | 712.7135 | 0 | 0 | 51.0302 | 558917.6463 | 0 | 28827.1359 | 51.4531 | 797954.0125 | 0.70044 | 123.8543
10:50 | -17.5 | -0.30543 | 0.75497 | 0.12641 | 0 | 0.95656 | 0.29584 | 16.9506 | 0.045416 | 0.99228 | 19.1113 | 717.4175 | 0 | 0 | 51.4531 | 563148.432 | 0 | 29207.8316 | 51.8792 | 803220.6238 | 0.70111 | 124.6157
10:55 | -16.25 | -0.28362 | 0.75998 | 0.12725 | 0 | 0.96241 | 0.27506 | 15.7597 | 0.039059 | 0.99336 | 19.1724 | 721.8069 | 0 | 0 | 51.8792 | 567063.6701 | 0 | 29591.2923 | 52.3081 | 808134.9924 | 0.70169 | 125.3826
11:00 | -15 | -0.2618 | 0.76463 | 0.12802 | 0 | 0.96784 | 0.2543 | 14.5704 | 0.033229 | 0.99435 | 19.2315 | 725.8796 | 0 | 0 | 52.3081 | 570661.5546 | 0 | 29977.2894 | 52.7395 | 812694.7794 | 0.70218 | 126.1546
11:05 | -13.75 | -0.23998 | 0.76892 | 0.12874 | 0 | 0.97284 | 0.23358 | 13.3829 | 0.027913 | 0.99525 | 19.2886 | 729.6336 | 0 | 0 | 52.7395 | 573940.4301 | 0 | 30365.5932 | 53.1733 | 816897.8147 | 0.70259 | 126.9312
11:10 | -12.5 | -0.21817 | 0.77284 | 0.1294 | 0 | 0.97742 | 0.2129 | 12.1981 | 0.023098 | 0.99607 | 19.3436 | 733.0673 | 0 | 0 | 53.1733 | 576898.7935 | 0 | 30755.9729 | 53.6091 | 820742.0977 | 0.7029 | 127.7119
11:15 | -11.25 | -0.19635 | 0.77639 | 0.12999 | 0 | 0.98157 | 0.19228 | 11.0166 | 0.018774 | 0.99681 | 19.3966 | 736.1788 | 0 | 0 | 53.6091 | 579535.2936 | 0 | 31148.1969 | 54.0467 | 824225.7989 | 0.70313 | 128.4964
11:20 | -10 | -0.17453 | 0.77958 | 0.13053 | 0 | 0.98529 | 0.17174 | 9.8399 | 0.014931 | 0.99746 | 19.4475 | 738.9668 | 0 | 0 | 54.0467 | 581848.7326 | 0 | 31542.0327 | 54.4858 | 827347.2601 | 0.70327 | 129.2841
11:25 | -8.75 | -0.15272 | 0.78239 | 0.131 | 0 | 0.98857 | 0.15132 | 8.6699 | 0.011559 | 0.99804 | 19.4963 | 741.43 | 0 | 0 | 54.4858 | 583838.0664 | 0 | 31937.247 | 54.9262 | 830104.9958 | 0.70333 | 130.0745
11:30 | -7.5 | -0.1309 | 0.78483 | 0.13141 | 0 | 0.99142 | 0.13107 | 7.5097 | 0.0086514 | 0.99853 | 19.543 | 743.5671 | 0 | 0 | 54.9262 | 585502.405 | 0 | 32333.6062 | 55.3676 | 832497.6933 | 0.70331 | 130.8672
11:35 | -6.25 | -0.10908 | 0.7869 | 0.13175 | 0 | 0.99384 | 0.11109 | 6.3648 | 0.0062021 | 0.99895 | 19.5874 | 745.3771 | 0 | 0 | 55.3676 | 586841.0128 | 0 | 32730.8761 | 55.8098 | 834524.214 | 0.7032 | 131.6618
11:40 | -5 | -0.087266 | 0.78859 | 0.13204 | 0 | 0.99581 | 0.091549 | 5.2454 | 0.0042053 | 0.99929 | 19.6297 | 746.8592 | 0 | 0 | 55.8098 | 587853.3095 | 0 | 33128.822 | 56.2525 | 836183.5932 | 0.70302 | 132.4576
11:45 | -3.75 | -0.06545 | 0.78991 | 0.13226 | 0 | 0.99735 | 0.072813 | 4.1719 | 0.0026567 | 0.99955 | 19.6698 | 748.0127 | 0 | 0 | 56.2525 | 588538.8696 | 0 | 33527.209 | 56.6953 | 837475.0412 | 0.70275 | 133.2544
11:50 | -2.5 | -0.043633 | 0.79085 | 0.13241 | 0 | 0.99845 | 0.055696 | 3.1911 | 0.001553 | 0.99974 | 19.7077 | 748.837 | 0 | 0 | 56.6953 | 588897.4234 | 0 | 33925.8024 | 57.1382 | 838397.9434 | 0.70241 | 134.0516
11:55 | -1.25 | -0.021817 | 0.79142 | 0.13251 | 0 | 0.99911 | 0.042216 | 2.4188 | 0.00089176 | 0.99985 | 19.7433 | 749.3318 | 0 | 0 | 57.1382 | 588928.8565 | 0 | 34324.3669 | 57.5807 | 838951.8604 | 0.70198 | 134.8487
12:00 | 0 | 0 | 0.79161 | 0.13254 | 0 | 0.99933 | 0.036636 | 2.0991 | 0.00067149 | 0.99989 | 19.7767 | 749.4967 | 0 | 0 | 57.5807 | 588633.2103 | 0 | 34722.6679 | 58.0227 | 839136.5287 | 0.70147 | 135.6453
12:05 | 1.25 | 0.021817 | 0.79142 | 0.13251 | 0 | 0.99911 | 0.042216 | 2.4188 | 0.00089176 | 0.99985 | 19.8078 | 749.3318 | 0 | 0 | 58.0227 | 588010.6816 | 0 | 35120.4704 | 58.4639 | 838951.8604 | 0.70089 | 136.4409
12:10 | 2.5 | 0.043633 | 0.79085 | 0.13241 | 0 | 0.99845 | 0.055696 | 3.1911 | 0.001553 | 0.99974 | 19.8366 | 748.837 | 0 | 0 | 58.4639 | 587061.6226 | 0 | 35517.5402 | 58.904 | 838397.9434 | 0.70022 | 137.2351
12:15 | 3.75 | 0.06545 | 0.78991 | 0.13226 | 0 | 0.99735 | 0.072813 | 4.1719 | 0.0026567 | 0.99955 | 19.8631 | 748.0127 | 0 | 0 | 58.904 | 585786.5412 | 0 | 35913.6432 | 59.3428 | 837475.0412 | 0.69947 | 138.0273
12:20 | 5 | 0.087266 | 0.78859 | 0.13204 | 0 | 0.99581 | 0.091549 | 5.2454 | 0.0042053 | 0.99929 | 19.8873 | 746.8592 | 0 | 0 | 59.3428 | 584186.1001 | 0 | 36308.546 | 59.78 | 836183.5932 | 0.69863 | 138.8171
12:25 | 6.25 | 0.10908 | 0.7869 | 0.13175 | 0 | 0.99384 | 0.11109 | 6.3648 | 0.0062021 | 0.99895 | 19.9092 | 745.3771 | 0 | 0 | 59.78 | 582261.1168 | 0 | 36702.0158 | 60.2154 | 834524.214 | 0.69772 | 139.604
12:30 | 7.5 | 0.1309 | 0.78483 | 0.13141 | 0 | 0.99142 | 0.13107 | 7.5097 | 0.0086514 | 0.99853 | 19.9287 | 743.5671 | 0 | 0 | 60.2154 | 580012.5631 | 0 | 37093.8206 | 60.6486 | 832497.6933 | 0.69671 | 140.3876
12:35 | 8.75 | 0.15272 | 0.78239 | 0.131 | 0 | 0.98857 | 0.15132 | 8.6699 | 0.011559 | 0.99804 | 19.9459 | 741.43 | 0 | 0 | 60.6486 | 577441.5649 | 0 | 37483.7291 | 61.0795 | 830104.9958 | 0.69562 | 141.1675
12:40 | 10 | 0.17453 | 0.77958 | 0.13053 | 0 | 0.98529 | 0.17174 | 9.8399 | 0.014931 | 0.99746 | 19.9607 | 738.9668 | 0 | 0 | 61.0795 | 574549.4014 | 0 | 37871.5112 | 61.5077 | 827347.2601 | 0.69445 | 141.943
12:45 | 11.25 | 0.19635 | 0.77639 | 0.12999 | 0 | 0.98157 | 0.19228 | 11.0166 | 0.018774 | 0.99681 | 19.9732 | 736.1788 | 0 | 0 | 61.5077 | 571337.5044 | 0 | 38256.9378 | 61.9331 | 824225.7989 | 0.69318 | 142.7139
12:50 | 12.5 | 0.21817 | 0.77284 | 0.1294 | 0 | 0.97742 | 0.2129 | 12.1981 | 0.023098 | 0.99607 | 19.9833 | 733.0673 | 0 | 0 | 61.9331 | 567807.4581 | 0 | 38639.7808 | 62.3553 | 820742.0977 | 0.69182 | 143.4796
12:55 | 13.75 | 0.23998 | 0.76892 | 0.12874 | 0 | 0.97284 | 0.23358 | 13.3829 | 0.027913 | 0.99525 | 19.991 | 729.6336 | 0 | 0 | 62.3553 | 563960.9978 | 0 | 39019.8137 | 62.7742 | 816897.8147 | 0.69037 | 144.2396
13:00 | 15 | 0.2618 | 0.76463 | 0.12802 | 0 | 0.96784 | 0.2543 | 14.5704 | 0.033229 | 0.99435 | 19.9964 | 725.8796 | 0 | 0 | 62.7742 | 559800.0094 | 0 | 39396.8113 | 63.1895 | 812694.7794 | 0.68882 | 144.9936
13:05 | 16.25 | 0.28362 | 0.75998 | 0.12725 | 0 | 0.96241 | 0.27506 | 15.7597 | 0.039059 | 0.99336 | 19.9993 | 721.8069 | 0 | 0 | 63.1895 | 555326.5284 | 0 | 39770.5499 | 63.6009 | 808134.9924 | 0.68717 | 145.7411
13:10 | 17.5 | 0.30543 | 0.75497 | 0.12641 | 0 | 0.95656 | 0.29584 | 16.9506 | 0.045416 | 0.99228 | 19.9999 | 717.4175 | 0 | 0 | 63.6009 | 550542.7388 | 0 | 40140.8073 | 64.0082 | 803220.6238 | 0.68542 | 146.4816
13:15 | 18.75 | 0.32725 | 0.74959 | 0.12551 | 0 | 0.95028 | 0.31665 | 18.1426 | 0.052316 | 0.99111 | 19.9981 | 712.7135 | 0 | 0 | 64.0082 | 545450.9724 | 0 | 40507.3632 | 64.4111 | 797954.0125 | 0.68356 | 147.2147
13:20 | 20 | 0.34907 | 0.74387 | 0.12455 | 0 | 0.9436 | 0.33747 | 19.3355 | 0.059775 | 0.98984 | 19.994 | 707.6971 | 0 | 0 | 64.4111 | 540053.7075 | 0 | 40869.9991 | 64.8094 | 792337.6653 | 0.6816 | 147.94
13:25 | 21.25 | 0.37088 | 0.73778 | 0.12353 | 0 | 0.93649 | 0.3583 | 20.5291 | 0.067812 | 0.98847 | 19.9874 | 702.3707 | 0 | 0 | 64.8094 | 534353.5675 | 0 | 41228.4984 | 65.2029 | 786374.2552 | 0.67952 | 148.657
13:30 | 22.5 | 0.3927 | 0.73135 | 0.12245 | 0 | 0.92898 | 0.37914 | 21.7232 | 0.076447 | 0.987 | 19.9785 | 696.7369 | 0 | 0 | 65.2029 | 528353.3201 | 0 | 41582.6465 | 65.5914 | 780066.6204 | 0.67732 | 149.3653
13:35 | 23.75 | 0.41452 | 0.72457 | 0.12132 | 0 | 0.92106 | 0.39999 | 22.9178 | 0.0857 | 0.98543 | 19.9673 | 690.7983 | 0 | 0 | 65.5914 | 522055.8755 | 0 | 41932.2312 | 65.9745 | 773417.7631 | 0.675 | 150.0645
13:40 | 25 | 0.43633 | 0.71744 | 0.12012 | 0 | 0.91274 | 0.42085 | 24.1127 | 0.095598 | 0.98375 | 19.9536 | 684.5577 | 0 | 0 | 65.9745 | 515464.2856 | 0 | 42277.0421 | 66.3521 | 766430.8477 | 0.67255 | 150.7541
13:45 | 26.25 | 0.45815 | 0.70997 | 0.11887 | 0 | 0.90402 | 0.4417 | 25.3078 | 0.10616 | 0.98195 | 19.9376 | 678.0182 | 0 | 0 | 66.3521 | 508581.7418 | 0 | 42616.8715 | 66.7239 | 759109.1996 | 0.66997 | 151.4337
13:50 | 27.5 | 0.47997 | 0.70216 | 0.11757 | 0 | 0.89491 | 0.46257 | 26.5031 | 0.11743 | 0.98004 | 19.9192 | 671.1828 | 0 | 0 | 66.7239 | 501411.5743 | 0 | 42951.514 | 67.0897 | 751456.3036 | 0.66725 | 152.103
13:55 | 28.75 | 0.50178 | 0.69402 | 0.1162 | 0 | 0.88541 | 0.48343 | 27.6984 | 0.12942 | 0.978 | 19.8986 | 664.0548 | 0 | 0 | 67.0897 | 493957.2497 | 0 | 43280.7667 | 67.4494 | 743475.802 | 0.66439 | 152.7615
14:00 | 30 | 0.5236 | 0.68555 | 0.11478 | 0 | 0.87552 | 0.50429 | 28.8938 | 0.14218 | 0.97583 | 19.8755 | 656.6376 | 0 | 0 | 67.4494 | 486222.3702 | 0 | 43604.4296 | 67.8026 | 735171.493 | 0.66137 | 153.4089
14:05 | 31.25 | 0.54542 | 0.67675 | 0.11331 | 0 | 0.86525 | 0.52515 | 30.0892 | 0.15574 | 0.97352 | 19.8502 | 648.9347 | 0 | 0 | 67.8026 | 478210.671 | 0 | 43922.305 | 68.1491 | 726547.3292 | 0.6582 | 154.0446
14:10 | 32.5 | 0.56723 | 0.66763 | 0.11178 | 0 | 0.8546 | 0.54602 | 31.2845 | 0.17014 | 0.97108 | 19.8225 | 640.9498 | 0 | 0 | 68.1491 | 469926.0193 | 0 | 44234.1983 | 68.4888 | 717607.4151 | 0.65485 | 154.6684
14:15 | 33.75 | 0.58905 | 0.6582 | 0.1102 | 0 | 0.84358 | 0.56688 | 32.4796 | 0.18542 | 0.96848 | 19.7926 | 632.6867 | 0 | 0 | 68.4888 | 461372.4119 | 0 | 44539.9179 | 68.8214 | 708356.0057 | 0.65133 | 155.2798
14:20 | 35 | 0.61087 | 0.64845 | 0.10857 | 0 | 0.8322 | 0.58773 | 33.6747 | 0.20164 | 0.96572 | 19.7603 | 624.1493 | 0 | 0 | 68.8214 | 452553.9737 | 0 | 44839.2749 | 69.1468 | 698797.504 | 0.64762 | 155.8785
14:25 | 36.25 | 0.63268 | 0.63839 | 0.10689 | 0 | 0.82046 | 0.60859 | 34.8696 | 0.21884 | 0.9628 | 19.7258 | 615.3416 | 0 | 0 | 69.1468 | 443474.9554 | 0 | 45132.0838 | 69.4646 | 688936.4595 | 0.64371 | 156.4642
14:30 | 37.5 | 0.6545 | 0.62802 | 0.10515 | 0 | 0.80836 | 0.62944 | 36.0643 | 0.23708 | 0.9597 | 19.6891 | 606.2679 | 0 | 0 | 69.4646 | 434139.7317 | 0 | 45418.1622 | 69.7748 | 678777.5655 | 0.63959 | 157.0363
14:35 | 38.75 | 0.67632 | 0.61736 | 0.10337 | 0 | 0.79591 | 0.65029 | 37.2587 | 0.25642 | 0.95641 | 19.6501 | 596.9325 | 0 | 0 | 69.7748 | 424552.7993 | 0 | 45697.3307 | 70.0771 | 668325.657 | 0.63525 | 157.5947
14:40 | 40 | 0.69813 | 0.6064 | 0.10153 | 0 | 0.78312 | 0.67113 | 38.4529 | 0.27694 | 0.95292 | 19.6089 | 587.3399 | 0 | 0 | 70.0771 | 414718.7743 | 0 | 45969.4138 | 70.3714 | 657585.7086 | 0.63067 | 158.1388
14:45 | 41.25 | 0.71995 | 0.59516 | 0.09965 | 0 | 0.76999 | 0.69197 | 39.6468 | 0.29871 | 0.94922 | 19.5656 | 577.4945 | 0 | 0 | 70.3714 | 404642.3907 | 0 | 46234.2389 | 70.6574 | 646562.8319 | 0.62584 | 158.6685
14:50 | 42.5 | 0.74176 | 0.58363 | 0.097719 | 0 | 0.75653 | 0.7128 | 40.8403 | 0.32182 | 0.94529 | 19.52 | 567.4011 | 0 | 0 | 70.6574 | 394328.4973 | 0 | 46491.6373 | 70.9349 | 635262.2733 | 0.62073 | 159.1833
14:55 | 43.75 | 0.76358 | 0.57183 | 0.095743 | 0 | 0.74275 | 0.73362 | 42.0336 | 0.34634 | 0.94112 | 19.4723 | 557.0645 | 0 | 0 | 70.9349 | 383782.0563 | 0 | 46741.4437 | 71.2039 | 623689.4111 | 0.61534 | 159.6829
15:00 | 45 | 0.7854 | 0.55975 | 0.093721 | 0 | 0.72865 | 0.75444 | 43.2264 | 0.3724 | 0.93669 | 19.4224 | 546.4896 | 0 | 0 | 71.2039 | 373008.1402 | 0 | 46983.4965 | 71.464 | 611849.7534 | 0.60964 | 160.167
15:05 | 46.25 | 0.80721 | 0.54741 | 0.091654 | 0 | 0.71424 | 0.77526 | 44.4189 | 0.40009 | 0.93199 | 19.3705 | 535.6814 | 0 | 0 | 71.464 | 362011.9299 | 0 | 47217.638 | 71.7152 | 599748.9353 | 0.60361 | 160.6353
15:10 | 47.5 | 0.82903 | 0.5348 | 0.089543 | 0 | 0.69953 | 0.79606 | 45.6109 | 0.42954 | 0.92698 | 19.3165 | 524.6452 | 0 | 0 | 71.7152 | 350798.7118 | 0 | 47443.7141 | 71.9573 | 587392.7161 | 0.59721 | 161.0874
15:15 | 48.75 | 0.85085 | 0.52194 | 0.08739 | 0 | 0.68451 | 0.81686 | 46.8025 | 0.46089 | 0.92165 | 19.2604 | 513.386 | 0 | 0 | 71.9573 | 339373.8757 | 0 | 47661.5749 | 72.1901 | 574786.9767 | 0.59043 | 161.5231
15:20 | 50 | 0.87266 | 0.50883 | 0.085196 | 0 | 0.66921 | 0.83765 | 47.9937 | 0.49429 | 0.91597 | 19.2023 | 501.9094 | 0 | 0 | 72.1901 | 327742.9118 | 0 | 47871.0743 | 72.4134 | 561937.7167 | 0.58324 | 161.9421
15:25 | 51.25 | 0.89448 | 0.49548 | 0.082961 | 0 | 0.65363 | 0.85843 | 49.1843 | 0.52992 | 0.90991 | 19.1422 | 490.2207 | 0 | 0 | 72.4134 | 315911.4085 | 0 | 48072.0701 | 72.6271 | 548851.0517 | 0.57559 | 162.3441
15:30 | 52.5 | 0.9163 | 0.4819 | 0.080686 | 0 | 0.63777 | 0.8792 | 50.3745 | 0.56797 | 0.90345 | 19.0801 | 478.3255 | 0 | 0 | 72.6271 | 303885.0496 | 0 | 48264.4246 | 72.8311 | 535533.2103 | 0.56744 | 162.7288
15:35 | 53.75 | 0.93811 | 0.46808 | 0.078373 | 0 | 0.62164 | 0.89996 | 51.5641 | 0.60865 | 0.89653 | 19.0161 | 466.2295 | 0 | 0 | 72.8311 | 291669.6114 | 0 | 48448.0039 | 73.0252 | 521990.5309 | 0.55876 | 163.096
15:40 | 55 | 0.95993 | 0.45405 | 0.076022 | 0 | 0.60525 | 0.92071 | 52.7531 | 0.65221 | 0.88912 | 18.9502 | 453.9384 | 0 | 0 | 73.0252 | 279270.9602 | 0 | 48622.6787 | 73.2092 | 508229.4593 | 0.5495 | 163.4454
15:45 | 56.25 | 0.98175 | 0.43979 | 0.073636 | 0 | 0.58861 | 0.94146 | 53.9415 | 0.69892 | 0.88118 | 18.8824 | 441.4582 | 0 | 0 | 73.2092 | 266695.0494 | 0 | 48788.3236 | 73.3831 | 494256.5448 | 0.53959 | 163.7766
15:50 | 57.5 | 1.0036 | 0.42533 | 0.071214 | 0 | 0.57173 | 0.96219 | 55.1293 | 0.74909 | 0.87265 | 18.8127 | 428.7946 | 0 | 0 | 73.3831 | 253947.9166 | 0 | 48944.8179 | 73.5467 | 480078.4379 | 0.52897 | 164.0896
15:55 | 58.75 | 1.0254 | 0.41066 | 0.068759 | 0 | 0.55461 | 0.98291 | 56.3165 | 0.80308 | 0.86348 | 18.7412 | 415.9538 | 0 | 0 | 73.5467 | 241035.681 | 0 | 49092.0452 | 73.6999 | 465701.8866 | 0.51758 | 164.3841
16:00 | 60 | 1.0472 | 0.3958 | 0.066271 | 0 | 0.53726 | 1.0036 | 57.503 | 0.86131 | 0.85358 | 18.668 | 402.9419 | 0 | 0 | 73.6999 | 227964.5401 | 0 | 49229.8936 | 73.8425 | 451133.7333 | 0.50531 | 164.6598
16:05 | 61.25 | 1.069 | 0.38075 | 0.063751 | 0 | 0.51969 | 1.0243 | 58.6888 | 0.92424 | 0.84288 | 18.593 | 389.765 | 0 | 0 | 73.8425 | 214740.7671 | 0 | 49358.2556 | 73.9745 | 436380.9117 | 0.49209 | 164.9165
16:10 | 62.5 | 1.0908 | 0.36552 | 0.061201 | 0 | 0.50191 | 1.045 | 59.8738 | 0.99241 | 0.83129 | 18.5163 | 376.4295 | 0 | 0 | 73.9745 | 201370.7076 | 0 | 49477.0286 | 74.0957 | 421450.4433 | 0.4778 | 165.1541
16:15 | 63.75 | 1.1126 | 0.35012 | 0.058621 | 0 | 0.48392 | 1.0657 | 61.0581 | 1.0664 | 0.8187 | 18.4379 | 362.9416 | 0.3 | 1.8927e-05 | 74.0957 | 0 | 1388582.2742 | 49586.1142 | 72.9481 | 406349.4342 | 0 | 165.3722
16:20 | 65 | 1.1345 | 0.33455 | 0.056014 | 0 | 0.46574 | 1.0863 | 62.2416 | 1.1471 | 0.80499 | 18.3579 | 349.3079 | 0.4 | 2.5236e-05 | 72.9481 | 0 | 1815488.8226 | 48553.2632 | 71.4606 | 391085.0718 | 0 | 163.3065
16:25 | 66.25 | 1.1563 | 0.31882 | 0.05338 | 0 | 0.44738 | 1.107 | 63.4243 | 1.2352 | 0.79001 | 18.2763 | 335.5347 | 0.2 | 1.2618e-05 | 71.4606 | 0 | 884443.8852 | 47214.5621 | 70.7172 | 375664.6209 | 0 | 160.6291
16:30 | 67.5 | 1.1781 | 0.30293 | 0.050721 | 0 | 0.42884 | 1.1276 | 64.6061 | 1.3319 | 0.77358 | 18.1931 | 321.6286 | 0.2 | 1.2618e-05 | 70.7172 | 0 | 872798.1546 | 46545.472 | 69.9836 | 360095.4209 | 0 | 159.2909
16:35 | 68.75 | 1.1999 | 0.28691 | 0.048038 | 0 | 0.41013 | 1.1482 | 65.7871 | 1.4383 | 0.7555 | 18.1084 | 307.5964 | 0.2 | 1.2618e-05 | 69.9836 | 0 | 861306.3593 | 45885.2259 | 69.2597 | 344384.8819 | 0 | 157.9705
16:40 | 70 | 1.2217 | 0.27074 | 0.045332 | 0 | 0.39126 | 1.1688 | 66.9671 | 1.5558 | 0.73551 | 18.0222 | 293.4445 | 0.2 | 1.2618e-05 | 69.2597 | 0 | 849966.4645 | 45233.7072 | 68.5453 | 328540.4813 | 0 | 156.6674
16:45 | 71.25 | 1.2435 | 0.25445 | 0.042604 | 0 | 0.37224 | 1.1894 | 68.1462 | 1.6864 | 0.71331 | 17.9346 | 279.1798 | 0.1 | 6.309e-06 | 68.5453 | 0 | 419388.2312 | 44590.8003 | 68.1751 | 312569.7601 | 0 | 155.3816
16:50 | 72.5 | 1.2654 | 0.23804 | 0.039856 | 0 | 0.35308 | 1.2099 | 69.3243 | 1.8322 | 0.68852 | 17.8456 | 264.8091 | 0 | 0 | 68.1751 | 0 | 0 | 44257.584 | 68.1398 | 296480.3195 | 0 | 154.7152
16:55 | 73.75 | 1.2872 | 0.22151 | 0.037089 | 0 | 0.33379 | 1.2305 | 70.5013 | 1.9959 | 0.66069 | 17.7552 | 250.3392 | 0 | 0 | 68.1398 | 0 | 0 | 44225.7995 | 68.1045 | 280279.8172 | 0 | 154.6516
17:00 | 75 | 1.309 | 0.20488 | 0.034304 | 0 | 0.31437 | 1.251 | 71.6773 | 2.181 | 0.62923 | 17.6635 | 235.777 | 0 | 0 | 68.1045 | 0 | 0 | 44194.0378 | 68.0692 | 263975.9639 | 0 | 154.5881
17:05 | 76.25 | 1.3308 | 0.18815 | 0.031503 | 0 | 0.29484 | 1.2715 | 72.8521 | 2.3917 | 0.59341 | 17.5706 | 221.1294 | 0 | 0 | 68.0692 | 0 | 0 | 44162.2989 | 68.034 | 247576.5192 | 0 | 154.5246
17:10 | 77.5 | 1.3526 | 0.17133 | 0.028687 | 0 | 0.2752 | 1.292 | 74.0258 | 2.6337 | 0.55228 | 17.4764 | 206.4034 | 0 | 0 | 68.034 | 0 | 0 | 44130.5828 | 67.9988 | 231089.2883 | 0 | 154.4612
17:15 | 78.75 | 1.3744 | 0.15443 | 0.025857 | 0 | 0.25547 | 1.3125 | 75.1983 | 2.9143 | 0.50457 | 17.3811 | 191.606 | 0 | 0 | 67.9988 | 0 | 0 | 44098.8895 | 67.9636 | 214522.1185 | 0 | 154.3978
17:20 | 80 | 1.3963 | 0.13746 | 0.023016 | 0 | 0.23566 | 1.3329 | 76.3695 | 3.2434 | 0.44862 | 17.2846 | 176.7443 | 0 | 0 | 67.9636 | 0 | 0 | 44067.2189 | 67.9284 | 197882.8946 | 0 | 154.3344
17:25 | 81.25 | 1.4181 | 0.12042 | 0.020163 | 0 | 0.21577 | 1.3533 | 77.5395 | 3.6346 | 0.38211 | 17.187 | 161.8252 | 0 | 0 | 67.9284 | 0 | 0 | 44035.5711 | 67.8933 | 181179.536 | 0 | 154.2711
17:30 | 82.5 | 1.4399 | 0.10333 | 0.0173 | 0 | 0.19581 | 1.3737 | 78.7081 | 4.107 | 0.3018 | 17.0884 | 146.856 | 0 | 0 | 67.8933 | 0 | 0 | 44003.9461 | 67.8582 | 164419.9928 | 0 | 154.2079
17:35 | 83.75 | 1.4617 | 0.08618 | 0.014429 | 0 | 0.17579 | 1.3941 | 79.8753 | 4.6886 | 0.20295 | 16.9888 | 131.8437 | 0 | 0 | 67.8582 | 0 | 0 | 43972.3437 | 67.8231 | 147612.2414 | 0 | 154.1447
17:40 | 85 | 1.4835 | 0.068993 | 0.011552 | 0 | 0.15573 | 1.4144 | 81.041 | 5.4215 | 0.078349 | 16.8883 | 116.7955 | 0 | 0 | 67.8231 | 0 | 0 | 43940.764 | 67.788 | 130764.2815 | 0 | 154.0815
17:45 | 86.25 | 1.5053 | 0.051773 | 0.0086686 | 0 | 0.13562 | 1.4348 | 82.2053 | 6.3733 | -0.083458 | 16.7868 | 101.7186 | 0.1 | 6.309e-06 | 67.788 | 0 | 413456.5557 | 43909.207 | 67.423 | 113884.1318 | 0 | 154.0184
17:50 | 87.5 | 1.5272 | 0.034529 | 0.0057814 | 0 | 0.11549 | 1.455 | 83.3679 | 7.6585 | -0.30195 | 16.6846 | 86.6201 | 0.3 | 1.8927e-05 | 67.423 | 0 | 1231794.0592 | 43580.7402 | 66.4053 | 96979.8263 | 0 | 153.3615
17:55 | 88.75 | 1.549 | 0.017269 | 0.0028914 | 0 | 0.095343 | 1.4753 | 84.5289 | 9.4885 | -0.61304 | 16.5815 | 71.5072 | 0.2 | 1.2618e-05 | 66.4053 | 0 | 805253.8544 | 42664.8029 | 65.7287 | 80059.4106 | 0 | 151.5296
18:00 | 90 | 1.5708 | -2.7398e-13 | -4.5873e-14 | 0 | 0.075183 | 1.4955 | 85.6883 | 12.3009 | -1.0912 | 16.4776 | 56.387 | 0.2 | 1.2618e-05 | 65.7287 | 0 | 794654.8712 | 42055.8522 | 65.0611 | 63130.9378 | 0 | 150.3117
18:05 | 91.25 | 1.5926 | -0.017269 | -0.0028914 | 0 | 0.055023 | 1.5157 | 86.8458 | 17.1744 | -1.9196 | 16.373 | 0 | 0 | 0 | 65.0611 | 0 | 0 | 41454.9508 | 65.028 | 0 | 0 | 149.1099
18:10 | 92.5 | 1.6144 | -0.034529 | -0.0057814 | 0 | 0.034872 | 1.5359 | 88.0016 | 27.6763 | -3.705 | 16.2678 | 0 | 0 | 0 | 65.028 | 0 | 0 | 41425.179 | 64.9949 | 0 | 0 | 149.0504
18:15 | 93.75 | 1.6362 | -0.051773 | -0.0086686 | 0 | 0.014741 | 1.5561 | 89.1554 | 66.8395 | -10.3627 | 16.162 | 0 | 0 | 0 | 64.9949 | 0 | 0 | 41395.4286 | 64.9619 | 0 | 0 | 148.9909
18:20 | 95 | 1.6581 | -0.068993 | -0.011552 | 0 | -0.0053619 | 1.5762 | 90.3072 | -187.5003 | 32.875 | 16.0557 | 0 | 0 | 0 | 64.9619 | 0 | 0 | 41365.6996 | 64.9289 | 0 | 0 | 148.9314
18:25 | 96.25 | 1.6799 | -0.08618 | -0.014429 | 0 | -0.025426 | 1.5962 | 91.457 | -40.3295 | 7.856 | 15.9488 | 0 | 0 | 0 | 64.9289 | 0 | 0 | 41335.992 | 64.8959 | 0 | 0 | 148.872
18:30 | 97.5 | 1.7017 | -0.10333 | -0.0173 | 0 | -0.045443 | 1.6163 | 92.6046 | -23.0058 | 4.911 | 15.8415 | 0 | 0 | 0 | 64.8959 | 0 | 0 | 41306.3057 | 64.8629 | 0 | 0 | 148.8126
18:35 | 98.75 | 1.7235 | -0.12042 | -0.020163 | 0 | -0.065402 | 1.6362 | 93.7499 | -16.2902 | 3.7693 | 15.7338 | 0 | 0 | 0 | 64.8629 | 0 | 0 | 41276.6407 | 64.83 | 0 | 0 | 148.7533
18:40 | 100 | 1.7453 | -0.13746 | -0.023016 | 0 | -0.085294 | 1.6562 | 94.8929 | -12.7242 | 3.1631 | 15.6257 | 0 | 0 | 0 | 64.83 | 0 | 0 | 41246.997 | 64.7971 | 0 | 0 | 148.694
18:45 | 101.25 | 1.7671 | -0.15443 | -0.025857 | 0 | -0.10511 | 1.6761 | 96.0335 | -10.5139 | 2.7874 | 15.5173 | 0 | 0 | 0 | 64.7971 | 0 | 0 | 41217.3746 | 64.7642 | 0 | 0 | 148.6347
18:50 | 102.5 | 1.789 | -0.17133 | -0.028687 | 0 | -0.12484 | 1.696 | 97.1715 | -9.0103 | 2.5318 | 15.4087 | 0 | 0 | 0 | 64.7642 | 0 | 0 | 41187.7735 | 64.7313 | 0 | 0 | 148.5755
18:55 | 103.75 | 1.8108 | -0.18815 | -0.031503 | 0 | -0.14447 | 1.7158 | 98.3068 | -7.9217 | 2.3467 | 15.2999 | 0 | 0 | 0 | 64.7313 | 0 | 0 | 41158.1936 | 64.6985 | 0 | 0 | 148.5164
19:00 | 105 | 1.8326 | -0.20488 | -0.034304 | 0 | -0.164 | 1.7355 | 99.4394 | -7.0974 | 2.2066 | 15.191 | 0 | 0 | 0 | 64.6985 | 0 | 0 | 41128.635 | 64.6657 | 0 | 0 | 148.4573
19:05 | 106.25 | 1.8544 | -0.22151 | -0.037089 | 0 | -0.18342 | 1.7553 | 100.569 | -6.452 | 2.0968 | 15.0819 | 0 | 0 | 0 | 64.6657 | 0 | 0 | 41099.0976 | 64.6329 | 0 | 0 | 148.3982
19:10 | 107.5 | 1.8762 | -0.23804 | -0.039856 | 0 | -0.20271 | 1.7749 | 101.6957 | -5.9331 | 2.0086 | 14.9728 | 0 | 0 | 0 | 64.6329 | 0 | 0 | 41069.5814 | 64.6001 | 0 | 0 | 148.3392
19:15 | 108.75 | 1.898 | -0.25445 | -0.042604 | 0 | -0.22187 | 1.7945 | 102.8191 | -5.5071 | 1.9362 | 14.8638 | 0 | 0 | 0 | 64.6001 | 0 | 0 | 41040.0864 | 64.5673 | 0 | 0 | 148.2802
19:20 | 110 | 1.9199 | -0.27074 | -0.045332 | 0 | -0.24089 | 1.8141 | 103.9393 | -5.1512 | 1.8757 | 14.7548 | 0 | 0 | 0 | 64.5673 | 0 | 0 | 41010.6126 | 64.5346 | 0 | 0 | 148.2212
19:25 | 111.25 | 1.9417 | -0.28691 | -0.048038 | 0 | -0.25976 | 1.8336 | 105.056 | -4.8497 | 1.8244 | 14.6459 | 0 | 0 | 0 | 64.5346 | 0 | 0 | 40981.16 | 64.5019 | 0 | 0 | 148.1623
19:30 | 112.5 | 1.9635 | -0.30293 | -0.050721 | 0 | -0.27847 | 1.853 | 106.1691 | -4.591 | 1.7805 | 14.5372 | 0 | 0 | 0 | 64.5019 | 0 | 0 | 40951.7285 | 64.4692 | 0 | 0 | 148.1035
19:35 | 113.75 | 1.9853 | -0.31882 | -0.05338 | 0 | -0.29701 | 1.8724 | 107.2784 | -4.3668 | 1.7424 | 14.4287 | 0 | 0 | 0 | 64.4692 | 0 | 0 | 40922.3181 | 64.4366 | 0 | 0 | 148.0446
19:40 | 115 | 2.0071 | -0.33455 | -0.056014 | 0 | -0.31538 | 1.8917 | 108.3837 | -4.1708 | 1.709 | 14.3204 | 0 | 0 | 0 | 64.4366 | 0 | 0 | 40892.9289 | 64.404 | 0 | 0 | 147.9859
19:45 | 116.25 | 2.0289 | -0.35012 | -0.058621 | 0 | -0.33356 | 1.9109 | 109.4848 | -3.998 | 1.6797 | 14.2125 | 0 | 0 | 0 | 64.404 | 0 | 0 | 40863.5608 | 64.3713 | 0 | 0 | 147.9271
19:50 | 117.5 | 2.0508 | -0.36552 | -0.061201 | 0 | -0.35154 | 1.93 | 110.5816 | -3.8446 | 1.6536 | 14.105 | 0 | 0 | 0 | 64.3713 | 0 | 0 | 40834.2138 | 64.3388 | 0 | 0 | 147.8684
19:55 | 118.75 | 2.0726 | -0.38075 | -0.063751 | 0 | -0.36932 | 1.9491 | 111.6738 | -3.7077 | 1.6303 | 13.9979 | 0 | 0 | 0 | 64.3388 | 0 | 0 | 40804.8878 | 64.3062 | 0 | 0 | 147.8098
20:00 | 120 | 2.0944 | -0.3958 | -0.066271 | 0 | -0.38689 | 1.9681 | 112.7611 | -3.5847 | 1.6094 | 13.8913 | 0 | 0 | 0 | 64.3062 | 0 | 0 | 40775.5829 | 64.2737 | 0 | 0 | 147.7512
20:05 | 121.25 | 2.1162 | -0.41066 | -0.068759 | 0 | -0.40424 | 1.9869 | 113.8435 | -3.4738 | 1.5905 | 13.7852 | 0 | 0 | 0 | 64.2737 | 0 | 0 | 40746.2991 | 64.2412 | 0 | 0 | 147.6926
20:10 | 122.5 | 2.138 | -0.42533 | -0.071214 | 0 | -0.42136 | 2.0057 | 114.9205 | -3.3733 | 1.5735 | 13.6797 | 0 | 0 | 0 | 64.2412 | 0 | 0 | 40717.0363 | 64.2087 | 0 | 0 | 147.6341
20:15 | 123.75 | 2.1598 | -0.43979 | -0.073636 | 0 | -0.43825 | 2.0244 | 115.992 | -3.2818 | 1.5579 | 13.5748 | 0 | 0 | 0 | 64.2087 | 0 | 0 | 40687.7945 | 64.1762 | 0 | 0 | 147.5756
20:20 | 125 | 2.1817 | -0.45405 | -0.076022 | 0 | -0.45489 | 2.043 | 117.0576 | -3.1984 | 1.5437 | 13.4706 | 0 | 0 | 0 | 64.1762 | 0 | 0 | 40658.5737 | 64.1437 | 0 | 0 | 147.5171
20:25 | 126.25 | 2.2035 | -0.46808 | -0.078373 | 0 | -0.47127 | 2.0615 | 118.117 | -3.1219 | 1.5307 | 13.3671 | 0 | 0 | 0 | 64.1437 | 0 | 0 | 40629.3739 | 64.1113 | 0 | 0 | 147.4587
20:30 | 127.5 | 2.2253 | -0.4819 | -0.080686 | 0 | -0.4874 | 2.0799 | 119.17 | -3.0517 | 1.5188 | 13.2644 | 0 | 0 | 0 | 64.1113 | 0 | 0 | 40600.195 | 64.0789 | 0 | 0 | 147.4004
20:35 | 128.75 | 2.2471 | -0.49548 | -0.082961 | 0 | -0.50326 | 2.0982 | 120.2161 | -2.987 | 1.5078 | 13.1625 | 0 | 0 | 0 | 64.0789 | 0 | 0 | 40571.0371 | 64.0466 | 0 | 0 | 147.3421
20:40 | 130 | 2.2689 | -0.50883 | -0.085196 | 0 | -0.51885 | 2.1163 | 121.2549 | -2.9274 | 1.4976 | 13.0615 | 0 | 0 | 0 | 64.0466 | 0 | 0 | 40541.9002 | 64.0142 | 0 | 0 | 147.2838
20:45 | 131.25 | 2.2907 | -0.52194 | -0.08739 | 0 | -0.53415 | 2.1343 | 122.2862 | -2.8721 | 1.4883 | 12.9614 | 0 | 0 | 0 | 64.0142 | 0 | 0 | 40512.7842 | 63.9819 | 0 | 0 | 147.2256
20:50 | 132.5 | 2.3126 | -0.5348 | -0.089543 | 0 | -0.54916 | 2.1522 | 123.3095 | -2.821 | 1.4796 | 12.8623 | 0 | 0 | 0 | 63.9819 | 0 | 0 | 40483.6891 | 63.9496 | 0 | 0 | 147.1674
20:55 | 133.75 | 2.3344 | -0.54741 | -0.091654 | 0 | -0.56388 | 2.1699 | 124.3243 | -2.7734 | 1.4715 | 12.7642 | 0 | 0 | 0 | 63.9496 | 0 | 0 | 40454.6148 | 63.9173 | 0 | 0 | 147.1092
21:00 | 135 | 2.3562 | -0.55975 | -0.093721 | 0 | -0.57829 | 2.1874 | 125.3302 | -2.7292 | 1.464 | 12.6672 | 0 | 0 | 0 | 63.9173 | 0 | 0 | 40425.5615 | 63.885 | 0 | 0 | 147.0511
21:05 | 136.25 | 2.378 | -0.57183 | -0.095743 | 0 | -0.59239 | 2.2048 | 126.3266 | -2.6881 | 1.457 | 12.5713 | 0 | 0 | 0 | 63.885 | 0 | 0 | 40396.529 | 63.8528 | 0 | 0 | 146.9931
21:10 | 137.5 | 2.3998 | -0.58363 | -0.097719 | 0 | -0.60617 | 2.222 | 127.313 | -2.6497 | 1.4504 | 12.4765 | 0 | 0 | 0 | 63.8528 | 0 | 0 | 40367.5174 | 63.8206 | 0 | 0 | 146.935
21:15 | 138.75 | 2.4216 | -0.59516 | -0.09965 | 0 | -0.61963 | 2.2391 | 128.2889 | -2.6139 | 1.4444 | 12.383 | 0 | 0 | 0 | 63.8206 | 0 | 0 | 40338.5266 | 63.7884 | 0 | 0 | 146.8771
21:20 | 140 | 2.4435 | -0.6064 | -0.10153 | 0 | -0.63275 | 2.2559 | 129.2536 | -2.5804 | 1.4387 | 12.2906 | 0 | 0 | 0 | 63.7884 | 0 | 0 | 40309.5567 | 63.7562 | 0 | 0 | 146.8191
21:25 | 141.25 | 2.4653 | -0.61736 | -0.10337 | 0 | -0.64554 | 2.2725 | 130.2065 | -2.5491 | 1.4333 | 12.1996 | 0 | 0 | 0 | 63.7562 | 0 | 0 | 40280.6075 | 63.7241 | 0 | 0 | 146.7612
21:30 | 142.5 | 2.4871 | -0.62802 | -0.10515 | 0 | -0.65799 | 2.2889 | 131.1469 | -2.5198 | 1.4284 | 12.1099 | 0 | 0 | 0 | 63.7241 | 0 | 0 | 40251.6791 | 63.692 | 0 | 0 | 146.7034
21:35 | 143.75 | 2.5089 | -0.63839 | -0.10689 | 0 | -0.67009 | 2.3051 | 132.074 | -2.4923 | 1.4237 | 12.0216 | 0 | 0 | 0 | 63.692 | 0 | 0 | 40222.7716 | 63.6599 | 0 | 0 | 146.6455
21:40 | 145 | 2.5307 | -0.64845 | -0.10857 | 0 | -0.68183 | 2.3211 | 132.9871 | -2.4666 | 1.4193 | 11.9347 | 0 | 0 | 0 | 63.6599 | 0 | 0 | 40193.8847 | 63.6278 | 0 | 0 | 146.5878
21:45 | 146.25 | 2.5525 | -0.6582 | -0.1102 | 0 | -0.69322 | 2.3367 | 133.8853 | -2.4426 | 1.4152 | 11.8492 | 0 | 0 | 0 | 63.6278 | 0 | 0 | 40165.0186 | 63.5957 | 0 | 0 | 146.53
21:50 | 147.5 | 2.5744 | -0.66763 | -0.11178 | 0 | -0.70423 | 2.3521 | 134.7677 | -2.42 | 1.4114 | 11.7653 | 0 | 0 | 0 | 63.5957 | 0 | 0 | 40136.1733 | 63.5637 | 0 | 0 | 146.4723
21:55 | 148.75 | 2.5962 | -0.67675 | -0.11331 | 0 | -0.71488 | 2.3673 | 135.6334 | -2.3988 | 1.4078 | 11.6829 | 0 | 0 | 0 | 63.5637 | 0 | 0 | 40107.3486 | 63.5317 | 0 | 0 | 146.4147
22:00 | 150 | 2.618 | -0.68555 | -0.11478 | 0 | -0.72515 | 2.3821 | 136.4814 | -2.379 | 1.4044 | 11.6021 | 0 | 0 | 0 | 63.5317 | 0 | 0 | 40078.5447 | 63.4997 | 0 | 0 | 146.3571
22:05 | 151.25 | 2.6398 | -0.69402 | -0.1162 | 0 | -0.73504 | 2.3965 | 137.3107 | -2.3605 | 1.4013 | 11.5229 | 0 | 0 | 0 | 63.4997 | 0 | 0 | 40049.7615 | 63.4678 | 0 | 0 | 146.2995
22:10 | 152.5 | 2.6616 | -0.70216 | -0.11757 | 0 | -0.74454 | 2.4106 | 138.12 | -2.3431 | 1.3983 | 11.4453 | 0 | 0 | 0 | 63.4678 | 0 | 0 | 40020.9989 | 63.4358 | 0 | 0 | 146.242
22:15 | 153.75 | 2.6834 | -0.70997 | -0.11887 | 0 | -0.75366 | 2.4244 | 138.9083 | -2.3269 | 1.3956 | 11.3694 | 0 | 0 | 0 | 63.4358 | 0 | 0 | 39992.2569 | 63.4039 | 0 | 0 | 146.1845
22:20 | 155 | 2.7053 | -0.71744 | -0.12012 | 0 | -0.76238 | 2.4378 | 139.6743 | -2.3117 | 1.393 | 11.2953 | 0 | 0 | 0 | 63.4039 | 0 | 0 | 39963.5357 | 63.372 | 0 | 0 | 146.1271
22:25 | 156.25 | 2.7271 | -0.72457 | -0.12132 | 0 | -0.7707 | 2.4507 | 140.4167 | -2.2975 | 1.3906 | 11.2229 | 0 | 0 | 0 | 63.372 | 0 | 0 | 39934.835 | 63.3402 | 0 | 0 | 146.0697
22:30 | 157.5 | 2.7489 | -0.73135 | -0.12245 | 0 | -0.77862 | 2.4633 | 141.1341 | -2.2843 | 1.3883 | 11.1524 | 0 | 0 | 0 | 63.3402 | 0 | 0 | 39906.155 | 63.3083 | 0 | 0 | 146.0123
22:35 | 158.75 | 2.7707 | -0.73778 | -0.12353 | 0 | -0.78613 | 2.4753 | 141.8252 | -2.2721 | 1.3862 | 11.0836 | 0 | 0 | 0 | 63.3083 | 0 | 0 | 39877.4955 | 63.2765 | 0 | 0 | 145.955
22:40 | 160 | 2.7925 | -0.74387 | -0.12455 | 0 | -0.79323 | 2.4869 | 142.4885 | -2.2607 | 1.3843 | 11.0168 | 0 | 0 | 0 | 63.2765 | 0 | 0 | 39848.8567 | 63.2447 | 0 | 0 | 145.8977
22:45 | 161.25 | 2.8143 | -0.74959 | -0.12551 | 0 | -0.79992 | 2.498 | 143.1224 | -2.2501 | 1.3825 | 10.9518 | 0 | 0 | 0 | 63.2447 | 0 | 0 | 39820.2384 | 63.2129 | 0 | 0 | 145.8405
22:50 | 162.5 | 2.8362 | -0.75497 | -0.12641 | 0 | -0.80619 | 2.5085 | 143.7255 | -2.2404 | 1.3809 | 10.8887 | 0 | 0 | 0 | 63.2129 | 0 | 0 | 39791.6406 | 63.1812 | 0 | 0 | 145.7833
22:55 | 163.75 | 2.858 | -0.75998 | -0.12725 | 0 | -0.81204 | 2.5184 | 144.2961 | -2.2315 | 1.3793 | 10.8276 | 0 | 0 | 0 | 63.1812 | 0 | 0 | 39763.0634 | 63.1495 | 0 | 0 | 145.7261
23:00 | 165 | 2.8798 | -0.76463 | -0.12802 | 0 | -0.81747 | 2.5278 | 144.8327 | -2.2233 | 1.378 | 10.7685 | 0 | 0 | 0 | 63.1495 | 0 | 0 | 39734.5067 | 63.1177 | 0 | 0 | 145.669
23:05 | 166.25 | 2.9016 | -0.76892 | -0.12874 | 0 | -0.82248 | 2.5366 | 145.3338 | -2.2158 | 1.3767 | 10.7114 | 0 | 0 | 0 | 63.1177 | 0 | 0 | 39705.9706 | 63.0861 | 0 | 0 | 145.6119
23:10 | 167.5 | 2.9234 | -0.77284 | -0.1294 | 0 | -0.82706 | 2.5446 | 145.7977 | -2.2091 | 1.3755 | 10.6564 | 0 | 0 | 0 | 63.0861 | 0 | 0 | 39677.4549 | 63.0544 | 0 | 0 | 145.5549
23:15 | 168.75 | 2.9452 | -0.77639 | -0.12999 | 0 | -0.83121 | 2.5521 | 146.2229 | -2.2031 | 1.3745 | 10.6034 | 0 | 0 | 0 | 63.0544 | 0 | 0 | 39648.9597 | 63.0228 | 0 | 0 | 145.4979
23:20 | 170 | 2.9671 | -0.77958 | -0.13053 | 0 | -0.83492 | 2.5588 | 146.6079 | -2.1977 | 1.3736 | 10.5525 | 0 | 0 | 0 | 63.0228 | 0 | 0 | 39620.4849 | 62.9911 | 0 | 0 | 145.441
23:25 | 171.25 | 2.9889 | -0.78239 | -0.131 | 0 | -0.83821 | 2.5648 | 146.9514 | -2.193 | 1.3728 | 10.5037 | 0 | 0 | 0 | 62.9911 | 0 | 0 | 39592.0306 | 62.9596 | 0 | 0 | 145.3841
23:30 | 172.5 | 3.0107 | -0.78483 | -0.13141 | 0 | -0.84106 | 2.57 | 147.2519 | -2.189 | 1.3721 | 10.457 | 0 | 0 | 0 | 62.9596 | 0 | 0 | 39563.5968 | 62.928 | 0 | 0 | 145.3272
23:35 | 173.75 | 3.0325 | -0.7869 | -0.13175 | 0 | -0.84347 | 2.5745 | 147.5085 | -2.1856 | 1.3715 | 10.4126 | 0 | 0 | 0 | 62.928 | 0 | 0 | 39535.1834 | 62.8964 | 0 | 0 | 145.2704
23:40 | 175 | 3.0543 | -0.78859 | -0.13204 | 0 | -0.84545 | 2.5782 | 147.7198 | -2.1828 | 1.3711 | 10.3703 | 0 | 0 | 0 | 62.8964 | 0 | 0 | 39506.7903 | 62.8649 | 0 | 0 | 145.2136
23:45 | 176.25 | 3.0761 | -0.78991 | -0.13226 | 0 | -0.84698 | 2.5811 | 147.8852 | -2.1807 | 1.3707 | 10.3302 | 0 | 0 | 0 | 62.8649 | 0 | 0 | 39478.4177 | 62.8334 | 0 | 0 | 145.1568
23:50 | 177.5 | 3.098 | -0.79085 | -0.13241 | 0 | -0.84808 | 2.5832 | 148.0039 | -2.1791 | 1.3705 | 10.2923 | 0 | 0 | 0 | 62.8334 | 0 | 0 | 39450.0654 | 62.8019 | 0 | 0 | 145.1001
23:55 | 178.75 | 3.1198 | -0.79142 | -0.13251 | 0 | -0.84874 | 2.5844 | 148.0753 | -2.1782 | 1.3703 | 10.2567 | 0 | 0 | 0 | 62.8019 | 0 | 0 | 39421.7335 | 62.7705 | 0 | 0 | 145.0435
24:00 | -180 | -3.1416 | -0.79161 | -0.13254 | 0 | -0.84896 | 2.5848 | 148.0991 | -2.1779 | 1.3702 | 10.2233 | 0 | 0 | 0 | 62.7705 | 0 | 0 | 39393.422 | 62.739 | 0 | 0 | 144.9868
24:05 | -178.75 | -3.1198 | -0.79142 | -0.13251 | 0 | -0.84874 | 2.5844 | 148.0753 | -2.1782 | 1.3703 | 10.1922 | 0 | 0 | 0 | 62.739 | 0 | 0 | 39365.1308 | 62.7076 | 0 | 0 | 144.9303
24:10 | -177.5 | -3.098 | -0.79085 | -0.13241 | 0 | -0.84808 | 2.5832 | 148.0039 | -2.1791 | 1.3705 | 10.1634 | 0 | 0 | 0 | 62.7076 | 0 | 0 | 39336.8599 | 62.6762 | 0 | 0 | 144.8737
24:15 | -176.25 | -3.0761 | -0.78991 | -0.13226 | 0 | -0.84698 | 2.5811 | 147.8852 | -2.1807 | 1.3707 | 10.1369 | 0 | 0 | 0 | 62.6762 | 0 | 0 | 39308.6093 | 62.6449 | 0 | 0 | 144.8172
24:20 | -175 | -3.0543 | -0.78859 | -0.13204 | 0 | -0.84545 | 2.5782 | 147.7198 | -2.1828 | 1.3711 | 10.1127 | 0 | 0 | 0 | 62.6449 | 0 | 0 | 39280.379 | 62.6135 | 0 | 0 | 144.7608
24:25 | -173.75 | -3.0325 | -0.7869 | -0.13175 | 0 | -0.84347 | 2.5745 | 147.5085 | -2.1856 | 1.3715 | 10.0908 | 0 | 0 | 0 | 62.6135 | 0 | 0 | 39252.169 | 62.5822 | 0 | 0 | 144.7043
24:30 | -172.5 | -3.0107 | -0.78483 | -0.13141 | 0 | -0.84106 | 2.57 | 147.2519 | -2.189 | 1.3721 | 10.0713 | 0 | 0 | 0 | 62.5822 | 0 | 0 | 39223.9792 | 62.5509 | 0 | 0 | 144.648
24:35 | -171.25 | -2.9889 | -0.78239 | -0.131 | 0 | -0.83821 | 2.5648 | 146.9514 | -2.193 | 1.3728 | 10.0541 | 0 | 0 | 0 | 62.5509 | 0 | 0 | 39195.8096 | 62.5196 | 0 | 0 | 144.5916
24:40 | -170 | -2.9671 | -0.77958 | -0.13053 | 0 | -0.83492 | 2.5588 | 146.6079 | -2.1977 | 1.3736 | 10.0393 | 0 | 0 | 0 | 62.5196 | 0 | 0 | 39167.6604 | 62.4884 | 0 | 0 | 144.5353
24:45 | -168.75 | -2.9452 | -0.77639 | -0.12999 | 0 | -0.83121 | 2.5521 | 146.2229 | -2.2031 | 1.3745 | 10.0268 | 0 | 0 | 0 | 62.4884 | 0 | 0 | 39139.5313 | 62.4571 | 0 | 0 | 144.4791
24:50 | -167.5 | -2.9234 | -0.77284 | -0.1294 | 0 | -0.82706 | 2.5446 | 145.7977 | -2.2091 | 1.3755 | 10.0167 | 0 | 0 | 0 | 62.4571 | 0 | 0 | 39111.4224 | 62.4259 | 0 | 0 | 144.4228
24:55 | -166.25 | -2.9016 | -0.76892 | -0.12874 | 0 | -0.82248 | 2.5366 | 145.3338 | -2.2158 | 1.3767 | 10.009 | 0 | 0 | 0 | 62.4259 | 0 | 0 | 39083.3337 | 62.3947 | 0 | 0 | 144.3667
25:00 | -165 | -2.8798 | -0.76463 | -0.12802 | 0 | -0.81747 | 2.5278 | 144.8327 | -2.2233 | 1.378 | 10.0036 | 0 | 0 | 0 | 62.3947 | 0 | 0 | 39055.2652 | 62.3636 | 0 | 0 | 144.3105
25:05 | -163.75 | -2.858 | -0.75998 | -0.12725 | 0 | -0.81204 | 2.5184 | 144.2961 | -2.2315 | 1.3793 | 10.0007 | 0 | 0 | 0 | 62.3636 | 0 | 0 | 39027.2168 | 62.3324 | 0 | 0 | 144.2544
25:10 | -162.5 | -2.8362 | -0.75497 | -0.12641 | 0 | -0.80619 | 2.5085 | 143.7255 | -2.2404 | 1.3809 | 10.0001 | 0 | 0 | 0 | 62.3324 | 0 | 0 | 38999.1886 | 62.3013 | 0 | 0 | 144.1984
25:15 | -161.25 | -2.8143 | -0.74959 | -0.12551 | 0 | -0.79992 | 2.498 | 143.1224 | -2.2501 | 1.3825 | 10.0019 | 0 | 0 | 0 | 62.3013 | 0 | 0 | 38971.1805 | 62.2702 | 0 | 0 | 144.1424
25:20 | -160 | -2.7925 | -0.74387 | -0.12455 | 0 | -0.79323 | 2.4869 | 142.4885 | -2.2607 | 1.3843 | 10.006 | 0 | 0 | 0 | 62.2702 | 0 | 0 | 38943.1925 | 62.2391 | 0 | 0 | 144.0864
25:25 | -158.75 | -2.7707 | -0.73778 | -0.12353 | 0 | -0.78613 | 2.4753 | 141.8252 | -2.2721 | 1.3862 | 10.0126 | 0 | 0 | 0 | 62.2391 | 0 | 0 | 38915.2247 | 62.2081 | 0 | 0 | 144.0304
25:30 | -157.5 | -2.7489 | -0.73135 | -0.12245 | 0 | -0.77862 | 2.4633 | 141.1341 | -2.2843 | 1.3883 | 10.0215 | 0 | 0 | 0 | 62.2081 | 0 | 0 | 38887.2769 | 62.1771 | 0 | 0 | 143.9746
25:35 | -156.25 | -2.7271 | -0.72457 | -0.12132 | 0 | -0.7707 | 2.4507 | 140.4167 | -2.2975 | 1.3906 | 10.0327 | 0 | 0 | 0 | 62.1771 | 0 | 0 | 38859.3492 | 62.146 | 0 | 0 | 143.9187
25:40 | -155 | -2.7053 | -0.71744 | -0.12012 | 0 | -0.76238 | 2.4378 | 139.6743 | -2.3117 | 1.393 | 10.0464 | 0 | 0 | 0 | 62.146 | 0 | 0 | 38831.4415 | 62.1151 | 0 | 0 | 143.8629
25:45 | -153.75 | -2.6834 | -0.70997 | -0.11887 | 0 | -0.75366 | 2.4244 | 138.9083 | -2.3269 | 1.3956 | 10.0624 | 0 | 0 | 0 | 62.1151 | 0 | 0 | 38803.5539 | 62.0841 | 0 | 0 | 143.8071
25:50 | -152.5 | -2.6616 | -0.70216 | -0.11757 | 0 | -0.74454 | 2.4106 | 138.12 | -2.3431 | 1.3983 | 10.0808 | 0 | 0 | 0 | 62.0841 | 0 | 0 | 38775.6863 | 62.0532 | 0 | 0 | 143.7514
25:55 | -151.25 | -2.6398 | -0.69402 | -0.1162 | 0 | -0.73504 | 2.3965 | 137.3107 | -2.3605 | 1.4013 | 10.1014 | 0 | 0 | 0 | 62.0532 | 0 | 0 | 38747.8387 | 62.0222 | 0 | 0 | 143.6957
26:00 | -150 | -2.618 | -0.68555 | -0.11478 | 0 | -0.72515 | 2.3821 | 136.4814 | -2.379 | 1.4044 | 10.1245 | 0 | 0 | 0 | 62.0222 | 0 | 0 | 38720.0111 | 61.9913 | 0 | 0 | 143.64
26:05 | -148.75 | -2.5962 | -0.67675 | -0.11331 | 0 | -0.71488 | 2.3673 | 135.6334 | -2.3988 | 1.4078 | 10.1498 | 0 | 0 | 0 | 61.9913 | 0 | 0 | 38692.2035 | 61.9605 | 0 | 0 | 143.5844
26:10 | -147.5 | -2.5744 | -0.66763 | -0.11178 | 0 | -0.70423 | 2.3521 | 134.7677 | -2.42 | 1.4114 | 10.1775 | 0 | 0 | 0 | 61.9605 | 0 | 0 | 38664.4159 | 61.9296 | 0 | 0 | 143.5288
26:15 | -146.25 | -2.5525 | -0.6582 | -0.1102 | 0 | -0.69322 | 2.3367 | 133.8853 | -2.4426 | 1.4152 | 10.2074 | 0 | 0 | 0 | 61.9296 | 0 | 0 | 38636.6482 | 61.8988 | 0 | 0 | 143.4733
26:20 | -145 | -2.5307 | -0.64845 | -0.10857 | 0 | -0.68183 | 2.3211 | 132.9871 | -2.4666 | 1.4193 | 10.2397 | 0 | 0 | 0 | 61.8988 | 0 | 0 | 38608.9005 | 61.868 | 0 | 0 | 143.4178
26:25 | -143.75 | -2.5089 | -0.63839 | -0.10689 | 0 | -0.67009 | 2.3051 | 132.074 | -2.4923 | 1.4237 | 10.2742 | 0 | 0 | 0 | 61.868 | 0 | 0 | 38581.1727 | 61.8372 | 0 | 0 | 143.3623
26:30 | -142.5 | -2.4871 | -0.62802 | -0.10515 | 0 | -0.65799 | 2.2889 | 131.1469 | -2.5198 | 1.4284 | 10.3109 | 0 | 0 | 0 | 61.8372 | 0 | 0 | 38553.4648 | 61.8064 | 0 | 0 | 143.3069
26:35 | -141.25 | -2.4653 | -0.61736 | -0.10337 | 0 | -0.64554 | 2.2725 | 130.2065 | -2.5491 | 1.4333 | 10.3499 | 0 | 0 | 0 | 61.8064 | 0 | 0 | 38525.7769 | 61.7757 | 0 | 0 | 143.2516
26:40 | -140 | -2.4435 | -0.6064 | -0.10153 | 0 | -0.63275 | 2.2559 | 129.2536 | -2.5804 | 1.4387 | 10.3911 | 0 | 0 | 0 | 61.7757 | 0 | 0 | 38498.1088 | 61.745 | 0 | 0 | 143.1962
26:45 | -138.75 | -2.4216 | -0.59516 | -0.09965 | 0 | -0.61963 | 2.2391 | 128.2889 | -2.6139 | 1.4444 | 10.4344 | 0 | 0 | 0 | 61.745 | 0 | 0 | 38470.4605 | 61.7143 | 0 | 0 | 143.1409
26:50 | -137.5 | -2.3998 | -0.58363 | -0.097719 | 0 | -0.60617 | 2.222 | 127.313 | -2.6497 | 1.4504 | 10.48 | 0 | 0 | 0 | 61.7143 | 0 | 0 | 38442.8322 | 61.6836 | 0 | 0 | 143.0857
26:55 | -136.25 | -2.378 | -0.57183 | -0.095743 | 0 | -0.59239 | 2.2048 | 126.3266 | -2.6881 | 1.457 | 10.5277 | 0 | 0 | 0 | 61.6836 | 0 | 0 | 38415.2236 | 61.6529 | 0 | 0 | 143.0304
27:00 | -135 | -2.3562 | -0.55975 | -0.093721 | 0 | -0.57829 | 2.1874 | 125.3302 | -2.7292 | 1.464 | 10.5776 | 0 | 0 | 0 | 61.6529 | 0 | 0 | 38387.6349 | 61.6223 | 0 | 0 | 142.9753
27:05 | -133.75 | -2.3344 | -0.54741 | -0.091654 | 0 | -0.56388 | 2.1699 | 124.3243 | -2.7734 | 1.4715 | 10.6295 | 0 | 0 | 0 | 61.6223 | 0 | 0 | 38360.066 | 61.5917 | 0 | 0 | 142.9201
27:10 | -132.5 | -2.3126 | -0.5348 | -0.089543 | 0 | -0.54916 | 2.1522 | 123.3095 | -2.821 | 1.4796 | 10.6835 | 0 | 0 | 0 | 61.5917 | 0 | 0 | 38332.5169 | 61.5611 | 0 | 0 | 142.865
27:15 | -131.25 | -2.2907 | -0.52194 | -0.08739 | 0 | -0.53415 | 2.1343 | 122.2862 | -2.8721 | 1.4883 | 10.7396 | 0 | 0 | 0 | 61.5611 | 0 | 0 | 38304.9876 | 61.5305 | 0 | 0 | 142.81
27:20 | -130 | -2.2689 | -0.50883 | -0.085196 | 0 | -0.51885 | 2.1163 | 121.2549 | -2.9274 | 1.4976 | 10.7977 | 0 | 0 | 0 | 61.5305 | 0 | 0 | 38277.4781 | 61.5 | 0 | 0 | 142.755
27:25 | -128.75 | -2.2471 | -0.49548 | -0.082961 | 0 | -0.50326 | 2.0982 | 120.2161 | -2.987 | 1.5078 | 10.8578 | 0 | 0 | 0 | 61.5 | 0 | 0 | 38249.9883 | 61.4695 | 0 | 0 | 142.7
27:30 | -127.5 | -2.2253 | -0.4819 | -0.080686 | 0 | -0.4874 | 2.0799 | 119.17 | -3.0517 | 1.5188 | 10.9199 | 0 | 0 | 0 | 61.4695 | 0 | 0 | 38222.5183 | 61.439 | 0 | 0 | 142.645
27:35 | -126.25 | -2.2035 | -0.46808 | -0.078373 | 0 | -0.47127 | 2.0615 | 118.117 | -3.1219 | 1.5307 | 10.9839 | 0 | 0 | 0 | 61.439 | 0 | 0 | 38195.068 | 61.4085 | 0 | 0 | 142.5901
27:40 | -125 | -2.1817 | -0.45405 | -0.076022 | 0 | -0.45489 | 2.043 | 117.0576 | -3.1984 | 1.5437 | 11.0498 | 0 | 0 | 0 | 61.4085 | 0 | 0 | 38167.6374 | 61.378 | 0 | 0 | 142.5353
27:45 | -123.75 | -2.1598 | -0.43979 | -0.073636 | 0 | -0.43825 | 2.0244 | 115.992 | -3.2818 | 1.5579 | 11.1176 | 0 | 0 | 0 | 61.378 | 0 | 0 | 38140.2265 | 61.3476 | 0 | 0 | 142.4805
27:50 | -122.5 | -2.138 | -0.42533 | -0.071214 | 0 | -0.42136 | 2.0057 | 114.9205 | -3.3733 | 1.5735 | 11.1873 | 0 | 0 | 0 | 61.3476 | 0 | 0 | 38112.8353 | 61.3172 | 0 | 0 | 142.4257
27:55 | -121.25 | -2.1162 | -0.41066 | -0.068759 | 0 | -0.40424 | 1.9869 | 113.8435 | -3.4738 | 1.5905 | 11.2588 | 0 | 0 | 0 | 61.3172 | 0 | 0 | 38085.4638 | 61.2868 | 0 | 0 | 142.3709
28:00 | -120 | -2.0944 | -0.3958 | -0.066271 | 0 | -0.38689 | 1.9681 | 112.7611 | -3.5847 | 1.6094 | 11.332 | 0 | 0 | 0 | 61.2868 | 0 | 0 | 38058.1119 | 61.2564 | 0 | 0 | 142.3162
28:05 | -118.75 | -2.0726 | -0.38075 | -0.063751 | 0 | -0.36932 | 1.9491 | 111.6738 | -3.7077 | 1.6303 | 11.407 | 0 | 0 | 0 | 61.2564 | 0 | 0 | 38030.7796 | 61.2261 | 0 | 0 | 142.2616
28:10 | -117.5 | -2.0508 | -0.36552 | -0.061201 | 0 | -0.35154 | 1.93 | 110.5816 | -3.8446 | 1.6536 | 11.4837 | 0 | 0 | 0 | 61.2261 | 0 | 0 | 38003.467 | 61.1957 | 0 | 0 | 142.2069
28:15 | -116.25 | -2.0289 | -0.35012 | -0.058621 | 0 | -0.33356 | 1.9109 | 109.4848 | -3.998 | 1.6797 | 11.5621 | 0 | 0 | 0 | 61.1957 | 0 | 0 | 37976.174 | 61.1654 | 0 | 0 | 142.1523
28:20 | -115 | -2.0071 | -0.33455 | -0.056014 | 0 | -0.31538 | 1.8917 | 108.3837 | -4.1708 | 1.709 | 11.6421 | 0 | 0 | 0 | 61.1654 | 0 | 0 | 37948.9007 | 61.1352 | 0 | 0 | 142.0978
28:25 | -113.75 | -1.9853 | -0.31882 | -0.05338 | 0 | -0.29701 | 1.8724 | 107.2784 | -4.3668 | 1.7424 | 11.7237 | 0 | 0 | 0 | 61.1352 | 0 | 0 | 37921.6468 | 61.1049 | 0 | 0 | 142.0433
28:30 | -112.5 | -1.9635 | -0.30293 | -0.050721 | 0 | -0.27847 | 1.853 | 106.1691 | -4.591 | 1.7805 | 11.8069 | 0 | 0 | 0 | 61.1049 | 0 | 0 | 37894.4126 | 61.0747 | 0 | 0 | 141.9888
28:35 | -111.25 | -1.9417 | -0.28691 | -0.048038 | 0 | -0.25976 | 1.8336 | 105.056 | -4.8497 | 1.8244 | 11.8916 | 0 | 0 | 0 | 61.0747 | 0 | 0 | 37867.1979 | 61.0444 | 0 | 0 | 141.9344
28:40 | -110 | -1.9199 | -0.27074 | -0.045332 | 0 | -0.24089 | 1.8141 | 103.9393 | -5.1512 | 1.8757 | 11.9778 | 0 | 0 | 0 | 61.0444 | 0 | 0 | 37840.0028 | 61.0143 | 0 | 0 | 141.88
28:45 | -108.75 | -1.898 | -0.25445 | -0.042604 | 0 | -0.22187 | 1.7945 | 102.8191 | -5.5071 | 1.9362 | 12.0654 | 0 | 0 | 0 | 61.0143 | 0 | 0 | 37812.8272 | 60.9841 | 0 | 0 | 141.8257
28:50 | -107.5 | -1.8762 | -0.23804 | -0.039856 | 0 | -0.20271 | 1.7749 | 101.6957 | -5.9331 | 2.0086 | 12.1544 | 0 | 0 | 0 | 60.9841 | 0 | 0 | 37785.6711 | 60.9539 | 0 | 0 | 141.7713
28:55 | -106.25 | -1.8544 | -0.22151 | -0.037089 | 0 | -0.18342 | 1.7553 | 100.569 | -6.452 | 2.0968 | 12.2448 | 0 | 0 | 0 | 60.9539 | 0 | 0 | 37758.5346 | 60.9238 | 0 | 0 | 141.7171
29:00 | -105 | -1.8326 | -0.20488 | -0.034304 | 0 | -0.164 | 1.7355 | 99.4394 | -7.0974 | 2.2066 | 12.3365 | 0 | 0 | 0 | 60.9238 | 0 | 0 | 37731.4175 | 60.8937 | 0 | 0 | 141.6628
29:05 | -103.75 | -1.8108 | -0.18815 | -0.031503 | 0 | -0.14447 | 1.7158 | 98.3068 | -7.9217 | 2.3467 | 12.4294 | 0 | 0 | 0 | 60.8937 | 0 | 0 | 37704.3199 | 60.8636 | 0 | 0 | 141.6086
29:10 | -102.5 | -1.789 | -0.17133 | -0.028687 | 0 | -0.12484 | 1.696 | 97.1715 | -9.0103 | 2.5318 | 12.5236 | 0 | 0 | 0 | 60.8636 | 0 | 0 | 37677.2417 | 60.8335 | 0 | 0 | 141.5545
29:15 | -101.25 | -1.7671 | -0.15443 | -0.025857 | 0 | -0.10511 | 1.6761 | 96.0335 | -10.5139 | 2.7874 | 12.6189 | 0 | 0 | 0 | 60.8335 | 0 | 0 | 37650.183 | 60.8035 | 0 | 0 | 141.5004
29:20 | -100 | -1.7453 | -0.13746 | -0.023016 | 0 | -0.085294 | 1.6562 | 94.8929 | -12.7242 | 3.1631 | 12.7154 | 0 | 0 | 0 | 60.8035 | 0 | 0 | 37623.1437 | 60.7735 | 0 | 0 | 141.4463
29:25 | -98.75 | -1.7235 | -0.12042 | -0.020163 | 0 | -0.065402 | 1.6362 | 93.7499 | -16.2902 | 3.7693 | 12.813 | 0 | 0 | 0 | 60.7735 | 0 | 0 | 37596.1239 | 60.7435 | 0 | 0 | 141.3922
29:30 | -97.5 | -1.7017 | -0.10333 | -0.0173 | 0 | -0.045443 | 1.6163 | 92.6046 | -23.0058 | 4.911 | 12.9116 | 0 | 0 | 0 | 60.7435 | 0 | 0 | 37569.1234 | 60.7135 | 0 | 0 | 141.3382
29:35 | -96.25 | -1.6799 | -0.08618 | -0.014429 | 0 | -0.025426 | 1.5962 | 91.457 | -40.3295 | 7.856 | 13.0112 | 0 | 0 | 0 | 60.7135 | 0 | 0 | 37542.1424 | 60.6835 | 0 | 0 | 141.2843
29:40 | -95 | -1.6581 | -0.068993 | -0.011552 | 0 | -0.0053619 | 1.5762 | 90.3072 | -187.5003 | 32.875 | 13.1117 | 0 | 0 | 0 | 60.6835 | 0 | 0 | 37515.1807 | 60.6536 | 0 | 0 | 141.2304
29:45 | -93.75 | -1.6362 | -0.051773 | -0.0086686 | 0 | 0.014741 | 1.5561 | 89.1554 | 66.8395 | -10.3627 | 13.2132 | 0 | 0 | 0 | 60.6536 | 0 | 0 | 37488.2384 | 60.6237 | 0 | 0 | 141.1765
29:50 | -92.5 | -1.6144 | -0.034529 | -0.0057814 | 0 | 0.034872 | 1.5359 | 88.0016 | 27.6763 | -3.705 | 13.3154 | 0 | 0 | 0 | 60.6237 | 0 | 0 | 37461.3154 | 60.5938 | 0 | 0 | 141.1226
29:55 | -91.25 | -1.5926 | -0.017269 | -0.0028914 | 0 | 0.055023 | 1.5157 | 86.8458 | 17.1744 | -1.9196 | 13.4185 | 0 | 0 | 0 | 60.5938 | 0 | 0 | 37434.4118 | 60.5639 | 0 | 0 | 141.0688
30:00 | -90 | -1.5708 | 1.045e-12 | 1.7497e-13 | 0 | 0.075183 | 1.4955 | 85.6883 | 12.3009 | -1.0912 | 13.5224 | 0 | 0 | 0 | 60.5639 | 0 | 0 | 37407.5275 | 60.5341 | 0 | 0 | 141.0151
36:00
Note on B32: Fletcher Miller: You need to fill in this cell with a formula and drag it down. Be careful when you go past midnight!!
Note on D26: Fletcher Miller: This is the first term in the equation for cos theta. It does not depend on time of day
Note on D31: Fletcher Miller: These three terms for cos(theta) depend on time of day.
Note on J31: Fletcher Miller: The right value will appear here when you get cos(theta).
Note on K31: Fletcher Miller: you will need to calculate this based on cell J31 and information from the SRCC spec. sheet. This number will not be valid if theta is greater than 60 degrees. In that case, just ignore it.
Note on L31: Fletcher Miller: an ambient temperature variation will appear here when you get the hour angle input.
Note on M31: Fletcher Miller: This will fill in when you get the correct numbers in the previous cells.
Note on V31: Fletcher Miller: The right value will appear here when you get the other cells filled in.